## FULL ACOUSTIC MEASUREMENTS
ACOUSTIC MEASUREMENTS
Date:
Taken by:
| Room: | Room | Room | Room | Room | Room | Room | Room
P2 | Audio | TP 1 | TP 2 | TP 3 | Test Point | Test Point | Test Point | Test Point
P2.1 | Measure the ambient noise, A-weighted, slow, at each location on the test plan is recorded, along with the highest measurement and its location (just the number value). | 48
P2.2 | Measure RT60 in the room. Should be less than 0.5s for standard rooms and less than 0.4s for executive spaces. (Note: If this requirement is not met, be sure to note it in the COM Report and any potential room factors that contributed to the failure such as glass/hard walls, tile floor, marble table, etc.)(Note: Please list RT60 measurements for each octave.) Please note the acoustic scale worksheet. Max RT60 values of less than 0.5s are PASS (Green), more than 0.9s are FAIL (Red), but some need to be noted/escalated to the client's team: 0.5 - 0.7s (Yellow) and 0.7s - 0.9s (Orange) will affect perform, should be noted on the COM REPORT, and be communicated to the user team. | 0 | 0 | 0 | 0 | 0 | 0 | 0
63 Hz
125 Hz
250 Hz
500 Hz
1 kHz
2 kHz
4 kHz
8 kHz
| MIN | 0 | 0 | 0 | 0 | 0 | 0 | 0
| MAX | 0 | 0 | 0 | 0 | 0 | 0 | 0
P2.3 | Measure NC curve of the room. Should be less than NC30 at all points. (measured with no filter or "Z-filter", see NC worksheet)(Note: If this requirement is not met, be sure to note it on the COM Report and note any potential room factors that contributed to the failure such as air handlers, fans, loud equipment, etc.) Please note the acoustic scale worksheet. NC values of less than NC30 are PASS (Green), more than NC45 are FAIL (Red), but some need to be noted/escalated to the client's team: NC35 (Yellow) andNC40 (Orange) will affect perform, should be noted on the COM REPORT, and be communicated to the user team. Also, to keep formatting consistent, please use PASS, NOTE, or FAIL to start this item with the "NC-??" on the next line. | BEST NC-30 | PASS NC-?? | PASS NC-?? | PASS NC-?? | PASS NC-?? | PASS NC-?? | PASS NC-??
P2.4 | Measure room width for audio recording and note it here. | 37'-4"
P2.5 | Measure room length for audio recording and note it here. | 24'-7"
P2.6 | Measure ceiling height for audio recording and note it here. | 7'-6"
P2.7 | Measure the largest distance from a talker's mouth to the nearest microphone in the system in inches (just the number value). | 105
P2.8 | The level of a standard talker (60 dB@1m) heard at the microphone element will be (dB-SPL): | 51.3975 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
P2.9 | The SNR at the microphone is recommended to be 25 dB. This system will have a SNR at the microphone of (in dB): Please note the acoustic scale worksheet. SNR values of more than 25 dB are PASS (Green), less than 10 dB are FAIL (Red), but some need to be noted/escalated to the UCAV team: 20-25 dB (Yellow) and 10-20 dB (Orange) will affect perform, should be noted on the COM REPORT, and be communicated to the user team. | 3.3975 | #NUM! | #NUM! | #NUM! | #NUM! | #NUM! | #NUM!
P2.10 | (Only in severely transmissive spaces) Measure sound isolation of room. Should be greater than 45 dB isolation at each octave. (see STC worksheet) | N/A
P2.11 | At each location on the test plan a nominal operating level of 66 dB SPL (Sound Pressure Level) for conference speech “A” weighted at all listeners’ ears +/-2 dB ("Uniformity of Coverage") (or at least 15 dB above the ambient noise, A-weighted, whichever is greater). Take measurements with system volume at 50% and 100%. | 58.8/62.4
P2.13 | There is no distortion heard from the system at full volume. | PASS
P2.14 | There is no hiss heard from the Polycom or display loudspeakers at full volume. | PASS
P2.15 | For conferencing mode, at the 65 dB SPL listening level, the system can demonstrate full duplex operation, with no reports of echo or “speech trails” (as detected from the far end), tested at 50% and at 100%. | PASS

## Acoustics Scale
Checklist Version: | 2.3
| NC30 | NC35 | NC40 | NC45+ | RT60 < 0.5s | RT60: 0.5s - 0.7s | RT60: 0.7s - 0.9s | RT60 > 0.9s | > 25 dB SNR @ Mic | 20-25 dB SNR @ Mic | 10-20 dB SNR @ Mic | < 10 dB SNR @ Mic
Category | BEST | GOOD | FAIR | POOR | BEST | GOOD | FAIR | POOR | BEST | GOOD | FAIR | POOR
Target Performance Criteria | < NC30 | < NC30 | < NC30 | < NC30 | RT60 < 0.5s | RT60 < 0.5s | RT60 < 0.5s | RT60 < 0.5s | > 25 dB SNR @ Mic | > 25 dB SNR @ Mic | > 25 dB SNR @ Mic | > 25 dB SNR @ Mic
Potential Audio Issues | n/a | -One end may sound slightly louder during double talk -Slight echo heard during double talk | -One end will sound louder during double talk -Noticeable echo heard during double talk | -Sight echo heard when one side talking -Little or no double talk performance | n/a | -Slightly hollow/thin sound from the microphones -Slight echo heard during double talk | -Hollow/thin sound from the microphones, but intelligible -Echo heard during double talk | -Unintelligible speech capture from microphones -Challenging to understand what is being said | n/a | -One end may sound slightly louder during double talk -Slight echo heard during double talk | -One end will sound louder during double talk -Noticeable echo heard during double talk | -Sight echo heard when one side talking -Little or no double talk performance
Improvement Tactics | n/a | -Reduce noise in the room (HVAC, appliances, hall traffic, etc.) | -Reduce noise in the room (HVAC, appliances, hall traffic, etc.) | -Reduce noise in room -Consider changing the purpose of the room | n/a | -Reduce reflections in room (acoustical panels on 25% of wall surfaces) | -Reduce reflections in room (acoustical panels, carpeting, new furtniture, acoustical ceiling panels, etc.) | -Reduce reflections -Change room construction | n/a | -Reduce noise in the room (HVAC, appliances, hall traffic, etc.) | -Reduce noise in the room (HVAC, appliances, hall traffic, etc.) | -Reduce noise in room -Consider changing the purpose of the room
Escalation/Notification | none | -PM lets user team performance may not be ideal, but should be acceptable | -PM escalates to user team. -System performance will be compromised. -Consider a different design solution | -PM escalates to user team. -PM delivers CO for change in design solution | none | -PM lets user team performance may not be ideal, but should be acceptable | -PM escalates to user team. -System performance will be compromised. -Consider a different design solution | -PM escalates to user team. -PM delivers CO for change in design solution | none | -PM lets user team performance may not be ideal, but should be acceptable | -PM escalates to user team. -System performance will be compromised. -Consider a different design solution | -PM escalates to user team. -PM delivers CO for change in design solution
PLEASE NOTE: Client may not want to see simple "Pass/Fail" for acoustical testing results. Please use this color scale to grade the results for the NC, RT60, and Mic SNR results.

## NC-NEW
Noise Criteria Mapping Spreadsheet
NC # | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
NC70 | 83 | 79 | 75 | 73 | 71 | 70 | 69 | 68
NC65 | 80 | 75 | 71 | 68 | 66 | 64 | 63 | 62
NC60 | 77 | 71 | 67 | 63 | 61 | 59 | 58 | 57
NC55 | 74 | 67 | 62 | 58 | 56 | 54 | 53 | 52
NC50 | 71 | 64 | 58 | 54 | 51 | 49 | 48 | 47
NC45 | 67 | 60 | 54 | 49 | 46 | 44 | 43 | 42
NC40 | 64 | 56 | 50 | 45 | 41 | 39 | 38 | 37
NC35 | 60 | 52 | 45 | 40 | 36 | 34 | 33 | 32
NC30 | 57 | 48 | 41 | 35 | 31 | 29 | 28 | 27
NC25 | 54 | 44 | 37 | 31 | 27 | 24 | 22 | 21
NC20 | 51 | 40 | 34 | 26 | 22 | 19 | 17 | 16
NC15 | 47 | 36 | 29 | 22 | 18 | 14 | 12 | 11
Measured | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Meas. # | 63 | 125 | 250 | 500 | 1000 | 2000 | 4000 | 8000
1
2
3
4
5
6
7
8
9
10